## Parameters
name	FirstSolar_FS395_plus

		User	Data	Default	Final	Model					OP	STC	NOC				OP: 200W/m², 25.0°C		STC: 1000W/m², 25.0°C		NOC: 800W/m², 44.0°C
material			CdTe		CdTe			Semiconductor type (technology)		G	G	200	1000	800	W/m²	Reference Irradiance		V	I	V	I	V	I
isCPV				0	0		[bool.]	Determines whether diffuse irradiance is to be ignored		Ta0	Ta	20		20	°C	Reference Ambient Temperature		0.0	0.46	0.0	2.29	0.0	1.84
Nbpd			4	3	4			Number of Bypass Diodes per Module		vw0	vw	1		1	m/s	Reference wind speed		1.1	0.46	1.2	2.29	1.1	1.84
nJunct	njunct			1	1			Number of pn junctions		AM	AM	1.5	1.5	1.5		Air Mass at NOC		2.1	0.46	2.3	2.29	2.1	1.84
length			1200		1200		mm	Module length			Tc,model	26.5		45.9	°C			3.2	0.46	3.5	2.28	3.2	1.84
width			600		600		mm	Module width		Tc	Tc	25.0	25	45.9	°C	Cell Temperature		4.3	0.46	4.6	2.28	4.3	1.84
area	A		0.72		0.720		m²	Active PV area		UF	UF	1.0	1.0	1.0		Utilization factor		5.4	0.46	5.8	2.28	5.4	1.84
Ns	Ns		73		73			Number of cells in series					6.4	0.46	7.0	2.28	6.4	1.84
Np	Np		2		2			Number of cells in parallel		Pmp	Pmp	18.49	95.0	70.6	W	MPP power		7.5	0.46	8.1	2.28	7.5	1.84
G_ref	Gref		1000	1000	1000		W/m²	Reference Irradiance		Imp	Imp	0.413	2.06	1.66	A	MPP current		8.6	0.46	9.3	2.28	8.6	1.84
Tc_ref	Tc,ref		25	25	25		°C	Reference Cell Temperature		Vmp	Vmp	44.73	46.1	42.5	V	MPP voltage		9.7	0.46	10.4	2.28	9.7	1.84
AM_ref	AM0			1.5	1.5			Air Mass at reference conditions		Voc	Voc	53.62	58.0	53.7	V	Open Circuit Voltage		10.7	0.45	11.6	2.28	10.7	1.84
						Isc	Isc	0.458	2.29	1.84	A	Short Circuit Current		11.8	0.45	12.8	2.27	11.8	1.83
Pnom	Pnom		95.0		95.0			Nominal MPP power		eta	η	12.8%	13.2%	12.3%		MPP efficiency		12.9	0.45	13.9	2.27	12.9	1.83
Pmp_ref	Pmp,ref				95.1	95.0	W	Reference MPP power (from Vmp and Imp)		FF		0.753	0.716	0.714				13.9	0.45	15.1	2.27	14.0	1.83
Imp_ref	Imp,ref		2.08		2.080	2.061	A	Reference MPP current					15.0	0.45	16.2	2.27	15.0	1.83
Vmp_ref	Vmp,ref		45.7		45.70	46.08	V	Reference MPP voltage		Ge	Ge	0.20	1.00	0.80				16.1	0.45	17.4	2.27	16.1	1.83
Voc_ref	Voc,ref		58		58.00	58.00	V	Reference Open Circuit Voltage		Rsh	Rsh	6802	3950	4051	Ω	Shunt Resistance		17.2	0.45	18.6	2.27	17.2	1.83
Isc_ref	Isc,ref		2.29		2.290	2.287	A	Reference Short Circuit Current		Iph	IL	0.465	2.324	1.873	A	Photo current		18.2	0.45	19.7	2.27	18.2	1.83
eta_ref	ηref				13.2%	13.2%		Reference MPP efficiency		Io	Io	1.88E-09	1.88E-09	2.38E-08	A	Saturation current		19.3	0.45	20.9	2.26	19.3	1.83
						0.184%				n	n	1.49	1.49	1.49				20.4	0.45	22.0	2.26	20.4	1.82
						nVth	Vth	2.79	2.79	2.97	V	Thermal voltage		21.4	0.45	23.2	2.26	21.5	1.82
Iph_ref	IL,ref			2.324	2.324		A	Reference photo current		Eg	εg	1.5	1.500	1.500	eV	Bandgap energy		22.5	0.45	24.4	2.26	22.5	1.82
Io_ref	Io,ref			1.88E-09	1.88E-09		A	Reference saturation current					23.6	0.45	25.5	2.26	23.6	1.82
Rs	Rs		1.850		1.850		Ω	Series resistance		muVoc	μVoc	-0.392%	-0.328%	-0.370%	1/K			24.7	0.45	26.7	2.25	24.7	1.82
Rsh_ref	Rsh,ref		3950		3950.0		Ω	Reference Shunt Resistance		muIsc	μIsc	0.039%	0.039%	0.039%	1/K			25.7	0.45	27.8	2.25	25.8	1.82
nDiode	n		1.487	1.500	1.487			Diode quality factor		muPmp	μPmp	-0.433%	-0.367%	-0.444%	1/K			26.8	0.45	29.0	2.25	26.8	1.81
Gamma	n·njunct		1.49		1.49			Gamma factor (PVsyst)					27.9	0.45	30.2	2.24	27.9	1.81
nVth_ref	Vth,ref				2.79		V	Reference thermal voltage: Ns·n·k·Tc,ref /q			ΔTc	2.0	K					29.0	0.45	31.3	2.24	29.0	1.81
						ΔG	0.0	W/m²					30.0	0.45	32.5	2.24	30.1	1.81
muVoc	μVoc		-0.343%		-0.343%	-0.328%	1/K	Voc dependence with temperature: d(Voc/Voc,0)/dTc		Ge	Ge	0.20	1.00	0.80				31.1	0.45	33.6	2.23	31.1	1.81
					-198.94	-190.4	mV/K	(the same, different units)		Rsh	Rsh	6802	3950	4051	Ω			32.2	0.45	34.8	2.23	32.2	1.80
muIsc	μIsc		0.039%		0.039%	0.039%	1/K	Isc dependence with temperature: d(Isc/Isc,0)/dTc		Iph	IL	0.465	2.326	1.875	A			33.2	0.45	36.0	2.22	33.3	1.80
					0.89	0.89	mA/K	(the same, different units)		Io	Io	2.49E-09	2.49E-09	3.05E-08	A			34.3	0.44	37.1	2.22	34.4	1.79
muPmp	μPmp		-0.290%		-0.290%	-0.367%	1/K	Pmp dependence with temperature: d(Pmp/Pmp,0)/dTc		n	n	1.49	1.49	1.49				35.4	0.44	38.3	2.21	35.4	1.79
						nVth	Vth	2.81	2.81	2.99	V			36.5	0.44	39.4	2.20	36.5	1.78
muNdiode	μn	0.000%			0.000%		1/K	Linear derate for n, in pvSyst 'muGamma'		Eg	εg	1.500	1.500	1.500	eV			37.5	0.44	40.6	2.19	37.6	1.77
Eg_ref	εg,ref			1.500	1.500		eV	Bandgap energy at reference conditions		UF	UF	1.000	1.000	1.000				38.6	0.44	41.8	2.18	38.6	1.76
muEg	μεg			0.00%	0.00%		1/K	Bandgap dependence with temperature: d(εg/εg,0)/dTc					39.7	0.44	42.9	2.16	39.7	1.74
						k	k	8.62E-05			eV/K	Boltzmann Constant		40.8	0.43	44.1	2.13	40.8	1.72
di2mutau	di2/(μτ)eff		0.95	0.0	0.95		V	Recombination current coefficient					41.8	0.43	45.2	2.09	41.9	1.68
						Δμn	0.010%		ΔEg	0.01				42.9	0.43	46.4	2.05	42.9	1.64
Rsh_model		PVsyst (exponential)					44.0	0.42	47.6	1.98	44.0	1.59
Rsh_0	Rsh,0		11500	47400	11500		Ω	Rsh(E=0), for exponential Rsh irradiance correction		n	1.49		Eg	1.51				45.0	0.41	48.7	1.89	45.1	1.52
Rsh_exp	bRsh		4.8	5.5	4.8			Exponent for Rsh irradiance correction		nVth	2.81		Io	2.50E-09				46.1	0.40	49.9	1.78	46.2	1.43
Rsh_base	Rsh,ref*				3887.3		Ω			μPmp	-0.358%		μPmp	-0.372%				47.2	0.38	51.0	1.63	47.2	1.31
						μVoc	-0.319%		μVoc	-0.332%				48.3	0.35	52.2	1.45	48.3	1.16
Rev_model		PVsyst (quadratic)					49.3	0.32	53.4	1.23	49.4	0.99
Vbi	Vbi			65.7	65.7		V	Built-in Voltage (all cells)		ΔμPmp/Δμn	0.886		ΔμPmp/ΔEg	-0.004				50.4	0.27	54.5	0.97	50.5	0.79
Brev	brev		3.9E-03	2.7E-03	3.9E-03		A/V²	Reverse voltage characteristic factor (single cell)		ΔμVoc/Δμn	0.949		ΔμVoc/ΔEg	-0.004				51.5	0.20	55.7	0.68	51.5	0.55
Vbr	Vbr			0	0.0		V	Reverse breakdown voltage (single cell)					52.5	0.11	56.8	0.35	52.6	0.29
avalanche_a	a			0.16	0.16			Avalanche breakdown fraction			J	Δx	=	ε				53.6	0.00	58.0	0.00	53.7	0.00
avalanche_m	m			2.27	2.27			Avalanche breakdown exponent		0.886	-0.004	Δμn		0.077%	(μPmp)
						0.949	-0.004	ΔEg		-0.015%	(μVoc )
TaNOC	Ta,noc			20	20		W/m²
GNOC	Gnoc			800	800.0		°C			Suggested μn	-0.64%	0.087%
vwNOC	vw,noc			1.0	1.0		m/s			Suggested Eg	0.023
NOCT	Tc,noc			44	44.0	45.9	°C

Temp_model		SAPM
absort	α			0.9	0.9			Optical absorptivity
Uconst	Uc	28		29	28		Wm-2K	Global heat transfer coefficient (wind independent)
Uwind	Uw			0	0		Wsm-3K	Global Heat transfer coefficient (wind dependent)

Mounting	Glass/cell/glass - Open rack
a_wind	a			-3.5	-3.5			Sandia Cell Temp. model coefficient 'a'
b_wind	b			-0.1	-0.1			Sandia Cell Temp. model coefficient 'b'
delT	ΔT			3.0	3.0		K	Sandia Cell Temp. model coefficient ΔT

## Mod_Curves
Module Curves / Module Voltage [V] / Mdule Current [A]

## DefaultTables
Material	Eg_ref	muEg	nJunct	Vbi· nJunct	Rshbase/Rsh0	Rshexp	nDiode ·nJunct	di2 mutau	Vbr	a	m
a-Si:H amorphous	1.7	0	1	0.9	12	5.5	1.4	1.4
a-Si:H single	1.7	0	1	0.9	12	5.5	1.4	1.4
a-Si:H tandem	1.7	0	2	1.8	12	5.5	2.8	1.4
a-Si:H tripple	1.7	0	3	2.7	12	5.5	4.2	1.4
CdTe	1.5	0	1	0.9	12	5.5	1.5	0
CIGS	1.12	0	1	0.9	12	5.5	1.3	0
CIS	1.03	0	1	0.9	12	5.5	1.5	0
CSG	1.12	0	1	0.9	12	5.5	1.3	0
EFG	1.12	0	1	0.9	4	5.5	1.4	0
AsGa	1.35	0	1	0.9	12	5.5	1.2	0
GaInP2/GaAs/Ge	1.35	0	1	0.9	12	5.5	1.2	0
HIT	1.12	0	1	0.9	4	5.5	1.3	0
ribbon	1.12	0	1	0.9	12	5.5	1.4	0
Si-mono	1.12	0	1	0.9	4	5.5	1.3	0	-18	0.16	2.27
Si-poly	1.12	0	1	0.9	4	5.5	1.4	0	-18	0.16	2.27
uCSi-aSi:H	1.7	0	1	0.9	12	5.5	2.8	0
other	1.12	0	1	0.9	12	5.5	1.2	0

Mounting	a_wind	b_wind	delT
22X Linear Concentrator - Tracker	-3	-0.13	13
Glass/cell/glass - Close roof mount	-3	-0.0471	1
Glass/cell/glass - Open rack	-3	-0.0594	3
Glass/cell/polymer sheet - Insulated back	-3	-0.0455	0
Glass/cell/polymer sheet - Open rack	-4	-0.075	3
Polymer/thin-film/steel - Open rack	-4	-0.113	3

## UF
UF_name	UF_SoitecCX500					Ambient Temperature [°C] / UFT					Tc	UFT	AM	UFAM	G	UFE
UF_wAM	wAM	0.4		Utilization Factor Parameters					0	0.26	0	0.33	0	0.14
UF_AMthld	AMthld	1.7		Air-Mass Dependent					5	0.27	0.5	0.35	50	0.15
UF_sAMhi	SAMhi	-0.1					10	0.28	1	0.37	100	0.16
UF_sAMlo	SAMlo	0.1					15	0.29	1.5	0.39	150	0.17
				20	0.29	2	0.39	200	0.18
UF_wT	wT	0.3		Utilization Factor Parameters					25	0.30	2.5	0.37	250	0.19
UF_Tthld	Tthld	25	°C	Temperature Dependent					30	0.30	3	0.35	300	0.20
UF_sThi	SThi	0	1/°C					Air Mass / UFAM					35	0.30	3.5	0.33	350	0.21
UF_sTlo	STlo	0.005	1/°C					40	0.30	4	0.31	400	0.22
				45	0.30	4.5	0.29	450	0.23
UF_wE	wE	0.3		Utilization Factor Parameters					50	0.30	5	0.27	500	0.24
UF_Ethld	Ethld	0.8	kW/m²	Irradiance Dependent					55	0.30	5.5	0.25	550	0.25
UF_sEhi	SEhi	0	m²/kW					60	0.30	6	0.23	600	0.26
UF_sElo	SElo	0.65	m²/kW					65	0.30	6.5	0.21	650	0.27
				70	0.30	7	0.19	700	0.28
UF_UF0	UF0	1.000	0.955	Utilization factor at reference conditions					75	0.30	7.5	0.17	750	0.29
				Irradiance [W/m²] / UFG					80	0.30	8	0.15	800	0.30
				85	0.30	8.5	0.13	850	0.30
				90	0.30	9	0.11	900	0.30
		OP	STC	NOC					95	0.30	9.5	0.09	950	0.30
G	G	200	1000	800	W/m²	Reference Irradiance					100	0.30	10	0.07	1000	0.30
Ta0	Ta	20	0.0	20	°C	Reference Ambient Temperature
vw0	vw	1	0	1	m/s	Reference wind speed
AM	AM	1.5	1.5	1.5		Air Mass at NOC

	UFAM	0.392	0.392	0.392
	UFT	0.293	0.263	0.293
	UFE	0.183	0.300	0.300
	UF	0.8675	0.9545	0.9845

## Output
Copy-paste this tables into new files with .samlib extension
Skip the first three lines to add them as entries of an existing library

library CustomODM	Variables	Format	Alias
type ODM
entries 1
entry FirstSolar_FS395_plus	name		name
01:pv.mod.odm.material=CdTe	material		source
02:pv.mod.odm.nJunct=1	nJunct	0
03:pv.mod.odm.isCPV=0	isCPV	0
04:pv.mod.odm.Nbpd=4	Nbpd	0
05:pv.mod.odm.area=0.72	area	0.0####	a_c
06:pv.mod.odm.width=600.0	width	0.0####
07:pv.mod.odm.length=1200.0	length	0.0####
08:pv.mod.odm.Ns=73	Ns	0	Ns
09:pv.mod.odm.Np=2	Np	0
10:pv.mod.odm.G_ref=1000.0	G_ref	0.0#
11:pv.mod.odm.Tc_ref=25.0	Tc_ref	0.0#
12:pv.mod.odm.AM_ref=1.5	AM_ref	0.0#
13:pv.mod.odm.Isc_ref=2.29	Isc_ref	0.0####	i_sc_ref
14:pv.mod.odm.Voc_ref=58.0	Voc_ref	0.0####	v_oc_ref
15:pv.mod.odm.Imp_ref=2.08	Imp_ref	0.0####	i_mp_ref
16:pv.mod.odm.Vmp_ref=45.7	Vmp_ref	0.0####	v_mp_ref
17:pv.mod.odm.Pmp_ref=95.056	Pmp_ref	0.0####
18:pv.mod.odm.eta_ref=0.13202	eta_ref	0.0####
19:pv.mod.odm.muIsc=3.9E-04	muIsc	0.0##E+##	alpha_sc
20:pv.mod.odm.muVoc=-3.43E-03	muVoc	0.0##E+##	beta_oc
21:pv.mod.odm.muPmp=-2.9E-03	muPmp	0.0##E+##	gamma_r
22:pv.mod.odm.nDiode=1.487	nDiode	0.0####
23:pv.mod.odm.Iph_ref=2.3242	Iph_ref	0.0####	IL_ref
24:pv.mod.odm.Io_ref=1.88E-09	Io_ref	0.0##E+##	I0_ref
25:pv.mod.odm.Rs=1.85	Rs	0.0####	Rs_ref
26:pv.mod.odm.Rsh_ref=3950.0	Rsh_ref	0.0####	Rsh_ref
27:pv.mod.odm.Eg_ref=1.5	Eg_ref	0.0####
28:pv.mod.odm.muEg=0.0E+00	muEg	0.0##E+##
29:pv.mod.odm.muNdiode=0.0E+00	muNdiode	0.0##E+##	adjust
30:pv.mod.odm.di2mutau=0.95	di2mutau	0.0##			di2mutau
31:pv.mod.odm.Vbi=65.7	Vbi	0.0#			Vbi
32:pv.mod.odm.Brev=3.92E-03	Brev	0.0##E+##			Vbr
33:pv.mod.odm.Rsh_0=11500.0	Rsh_0	0.0#			Rsh_0
34:pv.mod.odm.Rsh_exp=4.8	Rsh_exp	0.0#			Rsh_exp
		0.0#			avalanche_a
		0.0#			avalanche_m
35:pv.mod.odm.NOCT=44.0	NOCT	0.0#	t_noct
36:pv.mod.odm.TempModel=SAPM	TempModel
37:pv.mod.odm.a_wind=-3.47	a_wind	0.0#
38:pv.mod.odm.b_wind=-0.06	b_wind	0.0#
39:pv.mod.odm.delT=3.0	delT	0.0#
!

library CustomUF
type UF
entries 1
entry UF_SoitecCX500	UF_name
01:pv.mod.UF.wAM=0.4	UF_wAM	0.0#
02:pv.mod.UF.AMthld=1.7	UF_AMthld	0.0#
03:pv.mod.UF.sAMhi=-0.1	UF_sAMhi	0.0#
04:pv.mod.UF.sAMlo=0.1	UF_sAMlo	0.0#
05:pv.mod.UF.wT=0.3	UF_wT	0.0#
06:pv.mod.UF.Tthld=25.0	UF_Tthld	0.0#
07:pv.mod.UF.sThi=0.0	UF_sThi	0.0#
08:pv.mod.UF.sTlo=0.01	UF_sTlo	0.0#
09:pv.mod.UF.wE=0.3	UF_wE	0.0#
10:pv.mod.UF.Ethld=0.8	UF_Ethld	0.0#
11:pv.mod.UF.sEhi=0.0	UF_sEhi	0.0#
12:pv.mod.UF.sElo=0.65	UF_sElo	0.0#
!